## FMECA
[7 empty] | No | Yes | Random
[7 empty] | Yes | No | Aging
Number |  |  | Failure Mode & Mechanism |  | Effect |  |  |  |  | Maintenance Planning |  | Inspection Planning |  | Reference
System | Subsystem | Maintainable Unit | Failure Mode | Failure Mechanism (or Cause) | Local Effect | Global Effect | Hidden / Evident Failure | Dangerous Failure | Failure Development | Maintenance Task | Maintenance Interval | Inspection task | Inspection interval
Substructure of floating wind turbine | Mooring system | Mooring lines | Abnormal mooring line | Mooring lines wear | Mooring line strength decrease or broken | Plant shutdown, loss of position control, reduced stability | Yes | Yes | Aging | Replace | When required | General Visual Inspection (GVI) | 5Y | Bureau Veritas-NR 493 DT R03 E
Moring lines fatigue
Mooring lines corrosion
Abnormal stress
Not effective maintenance
|  |  | Mooring lines broken | Traditional chain wear | Malfunction of the whole system, the FOWT cannot locate in the water | Plant shutdown, loss of position control, reduced stability | Yes | Yes | Aging | Replace | When required | General Visual Inspection (GVI) | 5Y | Bureau Veritas-NR 493 DT R03 E
Friction chain wear
Mooring winch failure
Buoys friction chain wear
anchor pickup device damage
Hydraulic motor failure
Accumulator failure
Overpressure
Connectors failure
Mooring interface structure failure
Substructure of floating wind turbine | Mooring system | Fairlead | Fairlead failure | Fairlead corrosion | The anchor cannot be dropped and lift | No need for shutdown, need immediately maintenance | Yes | No | Aging | Replace, Repair | When required | Detailed Visual Inspection (DVI) | Within 1Y from start of operation (damage inspection). Additional inspections to be determined if significant changes found after this first inspection. Interval shall not exceed 5Y. | Bureau Veritas-NR 493 DT R03 E
Fairlead fatigue
Substructure of floating wind turbine | Mooring system | Anchor | Anchor failure | Abnormal working conditrions | Detaches from seabed | Plant shutdown, loss of position control | Yes | Yes | Aging | Replace, Repair | When required | Detailed Visual Inspection (DVI) | Within 1Y from start of operation (damage inspection). Additional inspections to be determined if significant changes found after this first inspection. Interval shall not exceed 5Y. | DNV GL-SE-0422
Cyclic degredation
Substructure of floating wind turbine | Floating Foundation | Brace structure | Watertight fault, broken braces | Inefficient detection | increased water level in bracestructure, leads to increased weight, increased stresses on structure | No need for shutdown, need immediately maintenance | Yes | No | Aging | Repair | When required | General Visual Inspection (GVI) | 5Y | DNVGL-ST-0119, in consideration of DNVGL-ST-0126
Pipe joint corrosion
Pipe joint weld defect
Pipe joint fatigue
Erosion
Breakage
Substructure of floating wind turbine | Floating Foundation | Pontoons and columns | Watertight fault | Inefficient detection | increased water level in pontoons and columns, increased weight, and unstable structure because of different water levels. | Plant shutdown | Yes | Yes | Aging | Repair | When required | General Visual Inspection (GVI) | 5Y | DNVGL-ST-0119, in consideration of DNVGL-ST-0126
Corrosion
Fatigue
Weld failures
Substructure of floating wind turbine | Electrical | Dynamic cables | Dynamic cables failure | Fatigue | No power or communication to plant | Plant shutdown | Yes | No | Aging | Replace, Repair | When required | First inspection as an "as-laid inspection", then GVI on later inspections. | Within 1Y from start of operation (damage inspection). Additional inspections to be determined if significant changes found after this first inspection. Interval shall not exceed 5Y. | DNVGL-RP-0360
Fishing activity
Overheating
Corrosion
Marine growth
Cuts on cable

## FFA
[5 empty] | 1 - Negligible | A - No Injury |  | A - Slight Pollution |  | A - Slight Loss |  | 1 - Very Low | 1 - Very Low | 1 - Very Low
[5 empty] | 2 - Low | B - Minor Injury |  | B - Minor Pollution |  | B - Minor Loss |  | 2 - Low | 2 - Low | 2 - Low
[5 empty] | 3 - Medium | C - Major Injury |  | C - Moderate Pollution |  | C - Moderate Loss |  | 3 - Medium | 3 - Medium | 3 - Medium
[5 empty] | 4 - High | D - Single Fatality |  | D - Major Pollution |  | D - Major Loss |  | 4 - High | 4 - High | 4 - High | Noncritical
[5 empty] | 5 - Expected | E - Multiple Fatality |  | E - Massive Pollution |  | E - Massive Loss |  | 5 - Very High | 5 - Very High | 5 - Very High | Critical
Number |  |  | Main Function |  | Probability of Failure | Consequence of Failure | [5 empty] | Risk |  |  | Critical / Noncritical
System | Subsystem | Maintainable Unit / Part | Functions | Failure Effect |  | Consequence of Failure (Safety) | Consequence of Failure (Safety) - Notes | Consequence of Failure (Environmental) | Consequence of Failure (Environmental) - Notes | Consequence of Failure (Economic) | Consequence of Failure (Economic) - Notes | Risk (Safety) | Risk (Environmental) | Risk (Economic)
Substructure of floating wind turbine | Mooring system | Mooring lines | Keep the structure in place, take loads from environment (currents, winds, and waves) | Malfunction of whole system, the FOWT cannot locate in water | 2 - Low | C - Major Injury | Danger for vessels nearby, and possible inspection & maintenance personnell | B - Minor Pollution | Minor pollution, no danger of chemical leaks | E - Massive Loss | Big economic loss, due to damage and cost of operations to get the turbine up and running | 3 - Medium | 2 - Low | 4 - High | Critical
Substructure of floating wind turbine | Mooring system | Anchors | Secure the wind turbine to seafloor | anchor failure, detaches from the seabed | 2 - Low | C - Major Injury | Danger for vessels nearby, and possible inspection & maintenance personnell | C - Moderate Pollution | Moderate pollution, no danger of chemical leaks, material leaks can occur, muddy sea | E - Massive Loss | Big economic loss, due to damage and cost of operations to get the turbine up and running | 3 - Medium | 2 - Low | 4 - High | Critical
Substructure of floating wind turbine | Mooring system | Fairlead | guide the mooring lines and anchor, drop and lift | Anchor and mooring lines cannot be dropped and lift | 3 - Medium | B - Minor Injury | Minor damage will occurr, no danger for nearby vessels | C - Moderate Pollution | Moderate pollution, no danger of chemical leaks, material leaks can occur | C - Moderate Loss | Moderate economic loss, not a major part of the FOWTs function | 3 - Medium | 3 - Medium | 3 - Medium | Critical
Substructure of floating wind turbine | Electrical | Dynamic cables | Deliver power/communication to the FOWT, and send power/communication onshore | No communication and power to the wind turbine | 2 - Low | A - No Injury | No damage will occurr to nearby vessels or possible inspection & maintenance personnel | C - Moderate Pollution | Moderate pollution, no danger of chemical leaks, material leaks can occur | D - Major Loss | Major economic loss, due to damage on electrical and time to fix | 1 - Very Low | 3 - Medium | 3 - Medium | Noncritical
Substructure of floating wind turbine | Floating Foundation | Pontoons and columns | Make the FOWT float and makes it very stable | Unstable structure, which can lead to capsizing | 2 - Low | E - Multiple Fatality | Hazardous. If personnel on board, death may occur. Can damage nearby vessels with people onboard | D - Major Pollution | Major pollution if capsizing, chemical leaks and material leaks(plastic etc.) | E - Massive Loss | Big economic loss, due to damage and cost of operations to get the turbine up and running | 4 - High | 3 - Medium | 4 - High | Critical
Substructure of floating wind turbine | Floating Foundation | Braces between pontoons and columns | keep the structure stable | can lead to more strain/stress on other components, which make it more unstable and lead to other failures | 2 - Low | B - Minor Injury | Minor damage will occurr, no danger for nearby vessels | A - Slight Pollution | Slight pollution, no chemical leaks | D - Major Loss | Major economic loss, due to damage on braces and time to fix | 2 - Low | 1 - Very Low | 3 - Medium | Noncritical
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40

## ROV
| What to inspect for (failure mechanisms) | Where to inspect (equipment) | How to inspect (method) | Difficulties with inspection | ROV type
Mooring lines (1st annual)
General inspection covers corrosion, damages, deformation, cracks, abrasions, dents, wear etc. which gives an overview over the conditions. DVI=Detailed Visual Inspection | General inspection | All over mooring system | Visual, DVI if necessary | Movement in mooring line | Freedom for visual inspection only, Liberty E-ROV or Isurus if need of work class ROV
| Marine growth | Top of mooring line | Visual inspection | Movement in mooring line
| Twist in chain/wire | Selected areas of mooring line | Visual inspection | Movement in mooring line, visibility to see twist over number of links
| Alingment of chain in fairleads | Fairleads | Visual inspection | Movement in mooring line, shallow water depth
| Trenches in proximity to anchors | Seabed close to anchors | Visual inspection | Movement in mooring line, visibility
| Misalignments in connections of mooring line | Connections of mooring line | Visual inspection | Movement in mooring line
| Interlink wear on chains | Selected interlinks on chain | Visual inspection | Movement in mooring line
Mooring lines (5 years annual)
| General inspection | All over mooring system | Visual inspection, Clean and DVI if necessary | Need to clean mooring line, Movement in mooring line | Liberty E-ROV, Isurus is recommended if harsh weather conditions at wind farm.
| Marine growth (extent and type) | All over mooring line | Visual inspection, clean if necessary | Movement
| Wear and tear, mismatch between chain links and fairlead pockets, twist beetween upper/lower fairleads | Fairleads, chain in fairleads | Visual inspection | Movement, shallow water depth
| Wear, plane bending, free movement | Fairleads, chain in fairleads | DVI | Movement, shallow water depth
| Diameter chain links | Every 100th link for general chain | Measurements for diameter | Movement
| Diameter chain links | Every link for chain in spalsh zone | Measurements for diameter | Movement
| Wear and scouring | Chain touchdown area (seabed) | Clean, DVI, measurements of scouring | Movement, visibility
| Wire breaks, fractures, rope diameter, wear and corrosion, deformation | Wire rope | DVI, measurements of corrosion rate and diameters | Movement
| Trenches in proximity to anchors | Anchor area | Visual inspection | Movement, visibility
| Wear, twist or other damages | Connectors, shackles, sockets etc | DVI | Movement
Floater hull
| General inspection | All over floating hull | Visual inspection | Shallow water depth | Liberty E-ROV, Isurus is recommended if harsh weather conditions at wind farm.
| Marine growth (extent and type) | All over floating hull | Visual inspection | Shallow water depth
| Corrosion | All over floating hull | DVI, measurements of corrosion rate | Shallow water depth
| Dents, deformations | All over floating hull | DVI | Shallow water depth
| Damage, worn out | Corrosion protection systems | DVI | Shallow water depth
Dynamic cable
| General inspection | All over dynamic cable | Visual inspection | Need to clean cable, movement of cable | Liberty E-ROV, Isurus is recommended if harsh weather conditions at wind farm.
| Marine growth (extent and type) | All over cable, floating elements | Visual inspection, clean if needed | Movement of cable
| Functionality and condition | Cable supports and guides | Visual inspection | Visibility, shallow depth

## Risk Matrix
CoF Ranking
CoF - Environmental |  | A - Slight Pollution | B - Minor Pollution | C - Moderate Pollution | D - Major Pollution | E - Massive Pollution
CoF - Economical |  | A - Slight Damage | B - Minor Damage | C - Moderate Damage | D - Major Damage | E - Massive Damage
CoF - Economical |  | A - Slight Loss | B - Minor Loss | C - Moderate Loss | D - Major Loss | E - Massive Loss
CoF - Safety |  | A - No Injury | B - Minor Injury | C - Major Injury | D - Single Fatality | E - Mulitple Fatality
PoF Ranking | 5 - Expected | 3 - Medium | 4 - High | 4 - High | 5 - Very High | 5 - Very High
| 4 - High | 3 - Medium | 3 - Medium | 4 - High | 4 - High | 5 - Very High
| 3 - Medium | 2 - Low | 3 - Medium | 3 - Medium | 4 - High | 4 - High
| 2 - Low | 1 - Very Low | 2 - Low | 3 - Medium | 3 - Medium | 4 - High
| 1 - Negligible | 1 - Very Low | 1 - Very Low | 2 - Low | 3 - Medium | 3 - Medium
CoF - Safety |  | No Injury | Minor injuries, with short recovery time | Injuries, with some recovery time | Serious injury with longer recovery time | Irreversible or fatal injury.
CoF - Safety |  | No Injury | Minor cuts, falling and getting a few scratches | Cuts that might need stitches, sprained ankles | Significant cuts, broken arms or legs | Serious head trauma, drowning
PoF |  | Rarely | Unikely | Possibly | Likely | Almost Certainly

## Translated table
Rank | CoF | PoF | Description of PoF
1 | No/very slight injury | P<=10^-5 | Extremely less/remote
2 | Slight injury | 10^-5<P<4*10^-4 | Very slight/slight
3 | Moderate/significant effect | 4*10^-4<P<1*10^-2 | Occasional/moderate
4 | Major effect | 10^-2<P<0.2 | Frequent/high
5 | Extreme/hazardous effect | P>0.2 | Very high/extremely high